Voltage Surge

A sudden rise in voltage for a very short duration on the power system is known as a voltage surge or transient voltage.

Transients or surges are of temporary nature and exist for a very short duration (a few hundred s) but they cause overvoltages on the power system. They originate from switching and from other causes but by far the most important transients are those caused by lightning striking a transmissionline. When lightning strikes a line, the surge rushes along the line, just as a flood of water rushes along a narrow valley when the retaining wall of a reservoir at its head suddenly gives way. In most of the cases, such surges may cause the line insulators (near the point where lightning has struck) to flash over and may also damage the nearby transformers, generators or other equipment connected to the line if the equipment is not suitably protected.

Fig. 24.1 shows the wave-form of a typical lightning surge. The voltage build-up is taken along

y-axis and the time along x-axis. It may be seen that lightning introduces a steep-fronted wave. The

steeper the wave front, the more rapid is the build-up of voltage at any point in the network. In most

of the cases, this build-up is comparatively rapid, being of the order of 1–5s. Voltage surges are

generally specified in terms of *rise time t1 and the time t2 to decay to half of the peak value. For

example, a 1/50 s surge is one which reaches its maximum value in 1s and decays to half of its peak

value is 50 s.

Causes of Overvoltages

The overvoltages on a power system may be broadly divided into two main categories viz.

1. Internal causes

(i) Switching surges (ii) Insulation failure

(iii) Arcing ground (iv) Resonance

2. External causes i.e. lightning

Internal causes do not produce surges of large magnitude. Experience shows that surges due to

internal causes hardly increase the system voltage to twice the normal value. Generally, surges due to

internal causes are taken care of by providing proper insulation to the equipment in the power system.

However, surges due to lightning are very severe and may increase the system voltage to several times

the normal value. If the equipment in the power system is not protected against lightning surges,

these surges may cause considerable damage. In fact, in a power system, the protective devices

provided against overvoltages mainly take care of lightning surges.

Internal Causes of Overvoltages

Internal causes of overvoltages on the power system are primarily due to oscillations set up by the

sudden changes in the circuit conditions. This circuit change may be a normal switching operation

such as opening of a circuit breaker, or it may be the fault condition such as grounding of a line

conductor. In practice, the normal system insulation is suitably designed to withstand such surges.

We shall briefly discuss the internal causes of overvoltages.

1. Switching Surges. The overvoltages produced on the power system due to switching

operations are known as switching surges. A few cases will be discussed by way of illustration :

(i) Case of an open line. During switching operations of an unloaded line, travelling waves are

set up which produce overvoltages on the line. As an illustration, consider an unloaded line being

connected to a voltage source as shown in Fig. 24.2.

When the unloaded line is connected to the voltage source, a voltage wave is set up which travels

along the line. On reaching the terminal point A, it is reflected back to the supply end without change

of sign. This causes voltage doubling i.e. voltage on the line becomes twice the normal value. If

Er.m.s. is the supply voltage, then instantaneous voltage which the line will have to withstand will be

2 √2 E . This overvoltage is of temporary nature. It is because the line losses attenuate the wave and

in a very short time, the line settles down to its normal supply voltage E. Similarly, if an unloaded line

is switched off, the line will attain a voltage of 2√2 E for a moment before settling down to the

normal value.

(ii) Case of a loaded line. Overvoltages will also be produced during the switching operations

of a loaded line. Suppose a loaded line is suddenly interrupted. This will set up a voltage of 2 Zn i

across the break (i.e. switch) where i is the instantaneous value of current at the time of opening of

line and *Zn is the natural impedance of the line. For example, suppose the line having Zn = 1000 Ωcarries a current of 100 A (r.m.s.) and the break occurs at the moment when current is maximum. The

voltage across the breaker (i.e. switch) = 2 √2  100 1000/1000 = 282·8 kV. If Vm is the peak value

of voltage in kV, the maximum voltage to which the line may be subjected is = (Vm + 282·8) kV.

(iii) Current chopping. Current chopping results in the production of high voltage transients

across the contacts of the air blast circuit breaker as detailed in chapter 19. It is briefly discussed

here. Unlike oil circuit breakers, which are independent for the effectiveness on the magnitude of the current being interrupted, air-blast circuit breakers retain the same extinguishing power irrespective

of the magnitude of this current. When breaking low currents (e.g. transformer magnetising current)

with air-blast breaker, the powerful de-ionising effect of air-blast causes the current to fall abruptly to

zero well before the natural current zero is reached. This phenomenon is called current chopping and

produces high transient voltage across the breaker contacts. Overvoltages due to current chopping

are prevented by resistance switching (See Chapter 19).

2. Insulation failure. The most common case of insulation failure in a power system is the

grounding of conductor (i.e. insulation failure between line and earth) which may cause overvoltages

in the system. This is illustrated in Fig. 24.3.

Suppose a line at potential E is earthed at point X. The earthing of the line causes two equal

voltages of E to travel along XQ and XP containing currents E/Zn and +E/Zn respectively. Both

these currents pass through X to earth so that current to earth is 2 E/Zn.

3. Arcing ground. In the early days of transmission, the neutral of three phase lines was not

earthed to gain two advantages. Firstly, in case of line-to-ground fault, the line is not put out of

action. Secondly, the zero sequence currents are eliminated, resulting in the decrease of interference

with communication lines. Insulated neutrals give no problem with short lines and comparatively low

voltages. However, when the lines are long and operate at high voltages, serious problem called

arcing ground is often witnessed. The arcing ground produces severe oscillations of three to four

times the normal voltage.

The phenomenon of intermittent arc taking place in line-to-ground fault of a 3 phase system with

consequent production of transients is known as arcing ground.

The transients produced due to arcing ground are cumulative and may cause serious damage to

the equipment in the power system by causing breakdown of insulation. Arcing ground can be prevented

by earthing the neutral.

4. Resonance. Resonance in an electrical system occurs when inductive reactance of the circuit

becomes equal to capacitive reactance. Under resonance, the impedance of the circuit is equal to

resistance of the circuit and the p.f. is unity. Resonance causes high voltages in the electrical system.

In the usual transmission lines, the capacitance is very small so that resonance rarely occurs at the

fundamental supply frequency. However, if generator e.m.f. wave is distorted, the trouble of resonance

may occur due to 5th or higher harmonics and in case of underground cables too.

24.4 Lightning

An electric discharge between cloud and earth, between clouds or between the charge centres of the

same cloud is known as lightning.

Lightning is a huge spark and takes place when clouds are charged to such a high potential (+ve

or −ve) with respect to earth or a neighbouring cloud that the dielectric strength of neighbouring

medium (air) is destroyed. There are several theories which exist to explain how the clouds acquire

charge. The most accepted one is that during the uprush of warm moist air from earth, the friction between the air and the tiny particles of water causes the building up of charges. When drops of water

are formed, the larger drops become positively charged and the smaller drops become negatively

charged. When the drops of water accumulate, they form clouds, and hence cloud may possess either

a positive or a negative charge, depending upon the charge of drops of water they contain. The charge

on a cloud may become so great that it may discharge to another cloud or to earth and we call this

discharge as lightning. The thunder which accompanies lightning is due to the fact that lightning

suddenly heats up the air, thereby causing it to expand. The surrounding air pushes the expanded air

back and forth causing the wave motion of air which we recognise as thunder.

Mechanism of Lightning Discharge

Let us now discuss the manner in which a lightning discharge occurs. When a charged cloud passes

over the earth, it induces equal and opposite charge on the earth below. Fig. 24.4 shows a negatively

charged cloud inducing a positive charge on the earth below it. As the charge acquired by the cloud

increases, the potential between cloud and earth increases and, therefore, gradient in the air increases.

When the potential gradient is sufficient (5 kV*/cm to 10 kV/cm) to break down the surrounding air,

the lightning stroke starts. The stroke mechanism is as under :

(i) As soon as the air near the cloud breaks down, a streamer called leader streamer or pilot

streamer starts from the cloud towards the earth and carries charge with it as shown in Fig.

24.4 (i). The leader streamer will continue its journey towards earth as long as the cloud,

from which it originates feeds enough charge to it to maintain gradient at the tip of leader

streamer above the strength of air. If this gradient is not maintained, the leader streamer

stops and the charge is dissipated without the formation of a complete stroke. In other

words, the leader streamer will not reach the earth. Fig. 24.4 (i) shows the leader streamer

being unable to reach the earth as gradient at its end cloud not be maintained above the

strength of air. It may be noted that current in the leader streamer is low (<100 A) and its

velocity of propagation is about 0·05% that of velocity of light. Moreover, the luminosity

of leader is also very low.

(ii) In many cases, the leader streamer continues its journey towards earth [See Fig. 24.4 (ii)]

until it makes contact with earth or some object on the earth. As the leader streamer moves

towards earth, it is accompanied by points of luminescence which travel in jumps giving rise to stepped leaders. The velocity of stepped leader exceeds one-sixth of that of light

and distance travelled in one step is about 50 m. It may be noted that stepped leaders have

sufficient luminosity and give rise to first visual phenomenon of discharge.

(iii) The path of leader streamer is a path of ionisation and, therefore, of complete breakdown

of insulation. As the leader streamer reaches near the earth, a return streamer shoots up

from the earth [See Fig. 24.4 (iii)] to the cloud, following the same path as the main channel

of the downward leader. The action can be compared with the closing of a switch between

the positive and negative terminals; the downward leader having negative charge and return

streamer the positive charge. This phenomenon causes a sudden spark which we call

lightning. With the resulting neutralisation of much of the negative charge on the cloud,

any further discharge from the cloud may have to originate from some other portion of it.

The following points may be noted about lightning discharge :

(a) A lightning discharge which usually appears to the eye as a single flash is in reality made up

of a number of separate strokes that travel down the same path. The interval between them

varies from 0·0005 to 0·5 second. Each separate stroke starts as a downward leader from

the cloud.

(b) It has been found that 87% of all lightning strokes result from negatively charged clouds

and only 13% originate from positively charged clouds.

(c) It has been estimated that throughout the world, there occur about 100 lightning strokes per

second.

(d) Lightning discharge may have currents in the range of 10 kA to 90 kA.

24.6 Types of Lightning Strokes

There are two main ways in which a lightning may strike the power system (e.g. overhead lines,

towers, sub-stations etc.), namely;

1. Direct stroke 2. Indirect stroke

1. Direct stroke. In the direct stroke, the lightning discharge (i.e. current path) is directly from

the cloud to the subject equipment e.g. an overhead line. From the line, the current path may be over

the insulators down the pole to the ground. The overvoltages set up due to the stroke may be large

enough to flashover this path directly to the ground. The direct strokes can be of two types viz.

(i) Stroke A and (ii) stroke B.

(i) In stroke A, the lightning discharge is from the cloud to the subject equipment i.e. an overhead

line in this case as shown in Fig. 24.5 (i). The cloud will induce a charge of opposite sign on the tall object (e.g. an overhead line in this case). When the potential between the

cloud and line exceeds the breakdown value of air, the lightning discharge occurs between

the cloud and the line.

(ii) In stroke B, the lightning discharge occurs on the overhead line as a result of stroke A

between the clouds as shown in Fig. 24.5 (ii). There are three clouds P, Q and R having

positive, negative and positive charges respectively. The charge on the cloud Q is bound

by the cloud R. If the cloud P shifts too near the cloud Q, then lightning discharge will

occur between them and charges on both these clouds disappear quickly. The result is that

charge on cloud R suddenly becomes free and it then discharges rapidly to earth, ignoring

tall objects.

Two points are worth noting about direct strokes. Firstly, direct strokes on the power system are

very rare. Secondly, stroke A will always occur on tall objects and hence protection can be provided

against it. However, stroke B completely ignores the height of the object and can even strike the

ground. Therefore, it is not possible to provide protection against stroke B.

2. Indirect stroke. Indirect strokes result from the electrostatically induced charges on the

conductors due to the presence of charged clouds. This is illustrated in Fig. 24.6. A positively

charged cloud is above the line and induces a negative charge on the line by electrostatic induction.

This negative charge, however, will be only on that portion of the line right under the cloud and the

portions of the line away from it will be positively charged as shown in Fig. 24.6. The induced

positive charge leaks slowly to earth via the insulators. When the cloud discharges to earth or to

another cloud, the negative charge on the wire is isolated as it cannot flow quickly to earth over the

insulators. The result is that negative charge rushes along the line is both directions in the form of

travelling waves. It may be worthwhile to mention here that majority of the surges in a transmission

line are caused by indirect lightning strokes.

Harmful Effects of Lightning

A direct or indirect lightning stroke on a transmission line produces a steep-fronted voltage wave on

the line. The voltage of this wave may rise from zero to peak value (perhaps 2000 kV) in about 1 μs

and decay to half the peak value in about 5μs. Such a steep-fronted voltage wave will initiate travelling

waves along the line in both directions with the velocity dependent upon the L and C parameters

of the line.

(i) The travelling waves produced due to lightning surges will shatter the insulators and may

even wreck poles.

(ii) If the travelling waves produced due to lightning hit the windings of a transformer or generator,

it may cause considerable damage. The inductance of the windings opposes any

sudden passage of electric charge through it. Therefore, the electric charges “piles up”

against the transformer (or generator). This induces such an excessive pressure between

the windings that insulation may breakdown, resulting in the production of arc. While the

normal voltage between the turns is never enough to start an arc, once the insulation has broken down and an arc has been started by a momentary overvoltage, the line voltage is

usually sufficient to maintain the arc long enough to severely damage the machine.

(iii) If the arc is initiated in any part of the power system by the lightning stroke, this arc will set

up very disturbing oscillations in the line. This may damage other equipment connected to

the line.

Lightning Arresters

The earthing screen and ground wires can well protect the electrical system against direct lightning

strokes but they fail to provide protection against travelling waves which may reach the terminal

apparatus. The lightning arresters or surge diverters provide protection against such surges.

A lightning arrester or a surge diverter is a protective device which conducts the high voltage

surges on the power system to the ground.

Fig. 24.8 (i) shows the basic form of a surge diverter. It consists of a spark gap in series with a

non-linear resistor. One end of the diverter is connected to the terminal of the equipment to be

protected and the other end is effectively grounded. The length of the gap is so set that normal line

voltage is not enough to cause an arc across the gap but a dangerously high voltage will break down

the air insulation and form an arc. The property of the non-linear resistance is that its resistance

decreases as the voltage (or current) increases and vice-versa. This is clear from the *volt/amp

characteristic of the resistor shown in Fig. 24.8 (ii).

Action. The action of the lightning arrester or surge diverter is as under :

(i) Under normal operation, the lightning arrester is off the line i.e. it conducts **no current to

earth or the gap is non-conducting.

(ii) On the occurrence of overvoltage, the air insulation across the gap breaks down and an arc

is formed, providing a low resistance path for the surge to the ground. In this way, the

excess charge on the line due to the surge is harmlessly conducted through the arrester to

the ground instead of being sent back over the line.

(iii) It is worthwhile to mention the function of non-linear resistor in the operation of arrester.

As the gap sparks over due to overvoltage, the arc would be a short-circuit on the power

system and may cause power-follow current in the arrester. Since the characteristic of the

resistor is to offer high resistance to high voltage (or current), it prevents the effect of a

short-circuit. After the surge is over, the resistor offers high resistance to make the gap

non-conducting.

Two things must be taken care of in the design of a lightning arrester. Firstly, when the surge is

over, the arc in gap should cease. If the arc does not go out, the current would continue to flow

through the resistor and both resistor and gap may be destroyed. Secondly, I R drop (where I is the

surge current) across the arrester when carrying surge current should not exceed the breakdown strength

of the insulation of the equipment to be protected.

24.12 Types of Lightning Arresters

There are several types of lightning arresters in general use. They differ only in constructional details but operate on the same principle viz. providing low resistance path for the surges to the ground. We

shall discuss the following types of lightning arresters :

1. Rod gap arrester 2. Horn gap arrester

3. Multigap arrester 4. Expulsion type lightning arrester

5. Valve type lightning arrester

1. Rod Gap Arrester. It is a very simple

type of diverter and consists of two 1·5 cm rods

which are bent at right angles with a gap inbetween

as shown in Fig. 24.9. One rod is connected to

the line circuit and the other rod is connected to

earth. The distance between gap and insulator

(i.e. distance P) must not be less than one-third of

the gap length so that the arc may not reach the

insulator and damage it. Generally, the gap length

is so adjusted that breakdown should occur at 80%

of spark- over voltage in order to avoid cascading

of very steep wave fronts across the insulators.

The string of insulators for an overhead line

on the bushing of transformer has frequently a rod

gap across it. Fig. 24.9 shows the rod gap across

the bushing of a transformer.

Under normal operating conditions, the gap

remains non-conducting. On the occurrence of a high voltage surge on the line, the gap sparks over

and the surge current is conducted to earth. In this way, excess charge on the line due to the surge is

harmlessly conducted to earth.

Limitations

(i) After the surge is over, the arc in the gap is maintained by the †normal supply voltage,

leading to a short-circuit on the system.

(ii) The rods may melt or get damaged due to excessive heat produced by the arc.

(iii) The climatic conditions (e.g. rain, humidity, temperature etc.) affect the performance of

rod gap arrester.

(iv) The polarity of the surge also affects the performance of this arrester.

Due to the above limitations, the rod gap arrester is only used as a ‘back-up’ protection in case of

main arresters.

2. Horn Gap Arrester. Fig. 24.10 shows the horn gap arrester. It consists of two horn shaped

metal rods A and B separated by a small air gap. The horns are so constructed that distance between

them gradually increases towards the top as shown. The horns are mounted on porcelain insulators.

One end of horn is connected to the line through a resistance R and choke coil L while the other end

is effectively grounded. The resistance R helps in limiting the follow current to a small value. The

choke coil is so designed that it offers small reactance at normal power frequency but a very high

reactance at transient frequency. Thus the choke does not allow the transients to enter the apparatus

to be protected. The gap between the horns is so adjusted that normal supply voltage is not enough to

cause an arc across the gap.

Under normal conditions, the gap is non-conducting i.e. normal supply voltage is insufficient to

initiate the arc between the gap. On the occurrence of an overvoltage, spark-over takes place across

the *small gap G. The heated air around the arc and the magnetic effect of the arc cause the arc to

travel up the gap. The arc moves progressively into positions 1, 2 and 3. At some position of the arc

(perhaps position 3), the distance may be too great for the voltage to maintain the arc. Consequently,

the arc is extinguished. The excess charge on the line is thus conducted through the arrester to the

ground.

Advantages

(i) The arc is self-clearing. Therefore, this type of arrester does not cause short-circuiting of

the system after the surge is over as in the case of rod gap.

(ii) Series resistance helps in limiting the follow current to a small value.

Limitations

(i) The bridging of gap by some external agency (e.g. birds) can render the device useless.

(ii) The setting of horn gap is likely to change due to corrosion or pitting. This adversely

affects the performance of the arrester.

(iii) The time of operation is comparatively long, say about 3 seconds. In view of the very short

operating time of modern protective gear for feeders, this time is far long.

Due to the above limitations, this type of arrester is not reliable and can only be used as a second

line of defence like the rod gap arrester.

3. Multigap arrester. Fig. 24.11 shows the multigap arrester. It consists of a series of metallic

(generally alloy of zinc) cylinders insulated from one another and separated by small intervals of air

gaps. The first cylinder (i.e. A) in the series is connected to the line and the other to the ground

through a series resistance. The series resistance limits the power arc. By the inclusion of series

resistance, the degree of protection against travelling waves is reduced. In order to overcome this

difficulty, some of the gaps (B to C in Fig. 24.11) are shunted by a resistance.

Under normal conditions, the point B is at earth potential and the normal supply voltage is unable

to break down the series gaps. On the occurrence of an overvoltage, the breakdown of series gaps A

to B occurs. The heavy current after breakdown will choose the straight - through path to earth via the

shunted gaps B and C, instead of the alternative path through the shunt resistance. When the surge is

over, the arcs B to C go out and any power current following the surge is limited by the two resistances

(shunt resistance and series resistance) which are now in series. The current is too small to maintain

the arcs in the gaps A to B and normal conditions are restored. Such arresters can be employed where

system voltage does not exceed 33 kV.

4. Expulsion type arrester. This type of arrester is also called ‘protector tube’ and is commonly

used on system operating at voltages upto 33 kV. Fig. 24.12 (i) shows the essential parts of an

expulsion type lightning arrester. It essentially consists of a rod gap A A′in series with a second gap

enclosed within the fibre tube. The gap in the fibre tube is formed by two electrodes. The upper

electrode is connected to rod gap and the lower electrode to the earth. One expulsion arrester is

placed under each line conductor. Fig. 24.12 (ii) shows the installation of expulsion arrester on an

overhead line.

On the occurrence of an overvoltage on the line, the series gap A A′is spanned and an arc is

struck between the electrodes in the tube. The heat of the arc vaporises some of the fibre of tube

walls, resulting in the production of a neutral gas*. In an extremely short time, the gas builds up high

pressure and is expelled through the lower electrode which is hollow. As the gas leaves the tube

violently, it carries away ionised air around the arc. This de-ionising effect is generally so strong that

arc goes out at a current zero and will not be re-established.

Advantages

(i) They are not very expensive.

(ii) They are improved form of rod gap arresters as they block the flow of power frequency

follow currents.

(iii) They can be easily installed.

Limitations

(i) An expulsion type arrester can perform only limited number of operations as during each

operation some of the fibre material is used up.

(ii) This type of arrester cannot be mounted in an enclosed equipment due to the discharge of

gases during operation.

(iii) Due to the poor volt/amp characteristic of the arrester, it is not suitable for the protection of

expensive equipment.

5. Valve type arrester. Valve type arresters incorporate non-linear resistors and are extensively

used on systems operating at high voltages. Fig. 24.13 (i) shows the various parts of a valve

type arrester. It consists of two assemblies (i) series spark gaps and (ii) non-linear resistor discs

(made of material such as thyrite or metrosil) in series. The non-linear elements are connected in

series with the spark gaps. Both the assemblies are accommodated in tight porcelain container.

(i) The spark gap is a multiple assembly consisting of a number of identical spark gaps in

series. Each gap consists of two electrodes with a fixed gap spacing. The voltage distribution

across the gaps is linearised by means of additional resistance elements (called grading

resistors) across the gaps. The spacing of the series gaps is such that it will withstand the

normal circuit voltage. However, an overvoltage will cause the gap to breakdown, causing

the surge current to ground via the non-linear resistors.

(ii) The non-linear resistor discs are made of an inorganic compound such as Thyrite or Metrosil.

These discs are connected in series. The non-linear resistors have the property of offering

a high resistance to current flow when normal system voltage is applied, but a low resistance

to the flow of high-surge currents. In other words, the resistance of these non-linear

elements decreases with the increase in current through them and vice-versa.

Working. Under normal conditions, the normal system voltage is insufficient to cause the breakdown

of air gap assembly. On the occurrence of an overvoltage, the breakdown of the series spark

gap takes place and the surge current is conducted to earth via the non-linear resistors. Since the

magnitude of surge current is very large, the non-linear elements will offer a very low resistance to the passage of surge. The result is that the surge will rapidly go to earth instead of being sent back over

the line. When the surge is over, the non-linear resistors assume high resistance to stop the flow of

current.

Advantages

(i) They provide very effective protection (especially for transformers and cables) against

surges.

(ii) They operate very rapidly taking less than a second.

(iii) The *impulse ratio is practically unity.

Limitations

(i) They **may fail to check the surges of very steep wave front from reaching the terminal

apparatus. This calls for additional steps to check steep-fronted waves.

(ii) Their performance is adversely affected by the entry of moisture into the enclosure. This

necessitates effective sealing of the enclosure at all times.

Applications. According to their application, the valve type arresters are classified as (i) station

type and (ii) line type. The station type arresters are generally used for the protection of important

equipment in power stations operating on voltages upto 220 kV or higher. The line type arresters are

also used for stations handling voltages upto 66 kV.

Surge Absorber

The travelling waves set up on the transmission lines

by the surges may reach the terminals apparatus and

cause damage to it. The amount of damage caused not

only depends upon the amplitude of the surge but also

upon the steepness of its wave front. The steeper the

wave front of the surge, the more the damage caused

to the equipment. In order to reduce the steepness of

the wave front of a surge, we generally use surge absorber.

A surge absorber is a protective device which

reduces the steepness of wave front of a surge by absorbing

surge energy.

Although both surge diverter and surge absorber

eliminate the surge, the manner in which it is done is

different in the two devices. The surge diverter diverts

the surge to earth but the surge absorber absorbs the

surge energy. A few cases of surge absorption are discussed

below :

(i) A condenser connected between the line and earth can act as a surge absorber. Fig. 24.14

shows how a capacitor acts as surge absorber to protect the transformer winding. Since the

reactance of a condenser is inversely proportional to frequency, it will be low at high frequency

and high at low frequency. Since the surges are of high frequency, the ***capacitor acts as a short circuit and passes them directly to earth. However, for power frequency, the

reactance of the capacitor is very high and practically no current flows to the ground.

(ii) Another type of surge absorber consists of a parallel combination of choke and resistance

connected in series with the line as shown in Fig. 24.15. The choke offers high reactance to

surge frequencies (XL = 2 f L). The surges are, therefore, forced

to flow through the resistance R where they are dissipated.

(iii) Fig. 24.16 shows the another type of surge absorber. It is called

Ferranti surge absorber. It consists of an air cored inductor connected

in series with the line. The inductor is surrounded by but

insulated from an earthed metallic sheet called dissipator. This arrangement

is equivalent to a transformer with short-circuited secondary.

The inductor forms the primary whereas the dissipator forms

the short-circuited secondary. The energy of the surge is used up in the form of heat generated

in the dissipator due to transformer action. This type of surge absorber is mainly used

for the protection of transformers.

Fig. 24.17 (i) shows the schematic diagram of 66 kV

Ferranti surge absorber while Fig. 24.17 (ii)

shows its equivalent circuit.