Protective Relays

A protective relay is a device that detects the fault and initiates the operation of the circuit breaker

to ioslate the defective element from the rest of the system.

The relays detect the abnormal conditions in the electrical circuits by constantly measuring the

electrical quantities which are different under normal and fault conditions. The electrical quantities

which may change under fault conditions are voltage, current, frequency and phase angle. Through

the changes in one or more of these quantities, the faults signal their presence, type and location to the

protective relays. Having detected the fault, the relay operates to close the trip circuit of the breaker.

This results in the opening of the breaker and disconnection of the faulty circuit.

Fundamental Requirements of Protective Relaying

The principal function of protective relaying is to cause the prompt removal from service of any

element of the power system when it starts to operate in an abnormal manner or interfere with the

effective operation of the rest of the system. In order that protective relay system may perform this

function satisfactorily, it should have the following qualities :

(i) selectivity (ii) speed (iii) sensitivity

(iv) reliability (v) simplicity (vi) economy

(i) Selectivity. It is the ability of the protective system to select correctly that part of the system

in trouble and disconnect the faulty part without disturbing the rest of the system.

(ii) Speed. The relay system should disconnect the faulty section as fast as possible for the

following reasons :

(a) Electrical apparatus may be damaged if they are made to carry the fault currents for a long

time.

(b) A failure on the system leads to a great reduction in the system voltage. If the faulty section

is not disconnected quickly, then the low voltage created by the fault may shut down consumers’

motors and the generators on the system may become unstable.

(c) The high speed relay system decreases the possibility of development of one type of fault

into the other more severe type.

(iii) Sensitivity. It is the ability of the relay system to operate with low value of actuating

quantity.

Sensitivity of a relay is a function of the volt-amperes input to the coil of the relay necessary to

cause its operation. The smaller the volt-ampere input required to cause relay operation, the more

sensitive is the relay. Thus, a 1 VA relay is more sensitive than a 3 VA relay. It is desirable that relay

system should be sensitive so that it operates with low values of volt-ampere input.

(iv) Reliability. It is the ability of the relay system to operate under the pre-determined conditions.

Without reliability, the protection would be rendered largely ineffective and could even become

a liability.

(v) Simplicity. The relaying system should be simple so that it can be easily maintained. Reliability

is closely related to simplicity. The simpler the protection scheme, the greater will be its

reliability.

(vi) Economy. The most important factor in the choice of a particular protection scheme is the

economic aspect. Sometimes it is economically unjustified to use an ideal scheme of protection and

a compromise method has to be adopted. As a rule, the protective gear should not cost more than 5%

of total cost. However, when the apparatus to be protected is of utmost importance (e.g. generator,

main transmission line etc.), economic considerations are often subordinated to reliability.

- Basic Relays

Most of the relays used in the power system operate by virtue of the current and/or voltage supplied

by current and voltage transformers connected in various combinations to the system element that is

to be protected. Through the individual or relative changes in these two quantities, faults signal their

presence, type and location to the protective relays. Having detected the fault, the relay operates the

trip circuit which results in the opening of the circuit breaker and hence in the disconnection of the

faulty circuit.

Most of the relays in service on electric power system today are of electro-mechanical type.

They work on the following two main operating principles :

(i) Electromagnetic attraction

(ii) Electromagnetic induction

Electromagnetic Attraction Relays

Electromagnetic attraction relays operate by virtue of an armature being attracted to the poles of an

electromagnet or a plunger being drawn into a solenoid. Such relays may be actuated by d.c. or a.c.

quantities. The important types of electromagnetic attraction relays are :

(i) Attracted armature type relay. Fig. 21.3 shows the

schematic arrangement of an attracted armature type relay. It

consists of a laminated electromagnet M carrying a coil C and

a pivoted laminated armature. The armature is balanced by a

counterweight and carries a pair of spring contact fingers at its

free end. Under normal operating conditions, the current

through the relay coil C is such that counterweight holds the

armature in the position shown. However, when a short-circuit

occurs, the current through the relay coil increases sufficiently

and the relay armature is attracted upwards. The contacts

on the relay armature bridge a pair of stationary contacts attached to the relay frame. This

completes the trip circuit which results in the opening of the circuit breaker and, therefore, in the

disconnection of the faulty circuit.

The minimum current at which the relay armature is attracted to close the trip circuit is called

pickup current. It is a usual practice to provide a number of tappings on the relay coil so that the

number of turns in use and hence the setting value at which the relay operates can be varied.

(ii) Solenoid type relay. Fig. 21.4 shows the schematic arrangement of a solenoid type relay. It

consists of a solenoid and movable iron plunger arranged as shown. Under normal operating conditions,

the current through the relay coil C is such that it holds the plunger by gravity or spring in the

position shown. However, on the occurrence of a fault, the current through the relay coil becomes

more than the pickup value, causing the plunger to be attracted to the solenoid. The upward movement of the plunger closes the trip circuit, thus opening the circuit breaker and disconnecting the faulty circuit.

(iii) Balanced beam type relay. It consists of an iron armature fastened to a balance beam. Under normal operating conditions,the current through the relay coil is such that the beamis held in the horizontal position by the spring. However, when a fault occurs, the current through the relay coil becomes greater than the pickup value and the beam is attracted to close the trip circuit. This causes the opening of the circuit breaker to isolate the faulty circuit.

Induction Relays

The following three types of structures are commonly used for obtaining the phase difference in

the fluxes and hence the operating torque in induction relays :

(i) shaded-pole structure

(ii) watthour-meter or double winding structure

(iii) induction cup structure

(i) Shaded-pole structure. The general arrangement of shaded-pole structure is shown in Fig.

21.7. It consists of a pivoted aluminium disc free to rotate in the air-gap of an electromagnet. Onehalf

of each pole of the magnet is surrounded by a copper band known as shading ring. The alternating

flux s in the shaded protion of the poles will, owing to the reaction of the current induced in the

ring, lag behind the flux u in the unshaded portion by an angle . These two a.c. fluxes differing in

phase will produce the necessary torque to rotate the disc.

This shows that driving torque is proportional to the square of current in the relay coil.

∝

(ii) Watthour-meter structure. This structure gets its name from the fact that it is used in watthour

meters. The general arrangement of this type of relay is shown in Fig. 21.8. It consists of a

pivoted aluminium disc arranged to rotate freely between the poles of two electromagnets. The upper

electromagnet carries two windings ; the pirmary and the secondary. The primary winding carries the

relay current I1 while the secondary winding is connected to the winding of the lower magnet. The

primary current induces e.m.f. in the secondary and so circulates a current I2 in it. The fluxϕ2 induced

in the lower magnet by the current in the secondary winding of the upper magnet will lag behind ϕ1 by

an angle α.The two fluxes ϕ1and ϕ2 differing in phase by will produce a driving torque on the disc

proportional to ϕ1ϕ2 sin α

An important feature of this type of relay is that its operation can be controlled by opening or

closing the secondary winding circuit. If this circuit is opened, no flux can be set by the lower magnet

however great the vaule of current in the pirmary winding may be and consequently no torque will be

produced. Therefore, the relay can be made inoperative by opening its secondary winding circuit.

(iii) Induction cup structure. Fig. 21.9 shows the general arrangement of an induction cup structure. It most closely resembles an induction motor, except that the rotor iron is stationary, only the rotor conductor portion being free to rotate. The moving element is a hollow cylindrical rotor which turns on its axis. The rotating field is produced by two pairs of coils wound on four poles as shown. The rotating field induces currents in the cup to provide the necessary driving torque. If ϕ 1 and ϕ 2 represent the fluxes produced by the respective pairs of

poles,then torque produced is proportional to ϕ 1 ϕ 2 sin α

where α is the phase difference between the two fluxes.

A control spring and the back stop for closing of the contactscarried

on an arm are attached to the spindle of the cup to prevent the continuous rotation.

Induction cup structures are more efficient torque producers than either

the shaded-pole or the watthour meter structures. Therefore, this type of relay has

very high speed and may have an operatingtime less then 0·1 second.

Important Terms

It is desirable to define and explain some important terms much used in connection with relays.

(i) Pick-up current. It is the minimum current in the relay coil at which the relay starts to

operate. So long as the current in the relay is less than the pick-up value, the relay does not operate

and the breaker controlled by it remains in the closed position. However, when the relay coil current

is equal to or greater than the pickup value, the relay

operates to energise the trip coil which opens the circuit

breaker.

(ii) Current setting. It is often desirable to adjust

the pick-up current to any required value. This is

known as current setting and is usually achieved by the

use of tappings on the relay operating coil. The taps

are brought out to a plug bridge as shown in Fig. 21.14.

The plug bridge permits to alter the number of turns on

the relay coil. This changes the torque on the disc and

hence the time of operation of the relay. The values

assigned to each tap are expressed in terms of percentage full-load rating of C.T. with which the relay

is associated and represents the value above which the disc commences to rotate and finally closes the

trip circuit.

∴Pick-up current = Rated secondary current of C.T. Current setting

For example, suppose that an overcurrent relay having current setting of 125% is connected to a

supply circuit through a current transformer of 400/5. The rated secondary current of C.T. is 5

amperes. Therefore, the pick-up value will be 25% more than 5 A i.e. 5 1·25 = 6·25 A. It means

that with above current setting, the relay will actually operate for a relay coil current equal to or

greater than 6·25 A.

The current plug settings usually range from 50% to 200% in steps of 25% for overcurrent relays

and 10% to 70% in steps of 10% for earth leakage relays. The desired current setting is obtained by

inserting a plug between the jaws of a bridge type socket at the tap value required.

(iii) Plug-setting multiplier (P.S.M.). It is the ratio of fault current in relay coil to the pick-up

current i.e.

P.S.M. =Fault current in relay coil/Pick - up current

=Fault current in relay coil /(Rated secondary current of CT Current setting)

(iv) Time-setting multiplier. A relay is generally provided with

control to adjust the time of operation. This adjustment is known as

time-setting multiplier. The time-setting dial is calibrated from 0 to 1 in

steps of 0.05 sec (see Fig. 21.15). These figures are multipliers to be

used to convert the time derived from time/P.S.M. curve into the actual

operating time. Thus if the time setting is 0·1 and the time obtained

from the time/P.S.M. curve is 3 seconds, then actual relay operating

time = 3 0·1 = 0·3 second. For instance, in an induction relay, the time

of operation is controlled by adjusting the amount of travel of the disc

from its reset position to its pickup position. This is achieved by the adjustment of the position of a

movable backstop which controls the travel of the disc and thereby varies the time in which the relay

will close its contacts for given values of fault current. A so-called “time dial” with an evenly divided

scale provides this adjustment. The acutal time of operation is calculated by multiplying the time

setting multiplier with the time obtained from time/P.S.M. curve of the relay.

Functional Relay Types

Most of the relays in service on power system today operate on the principle of electromagnetic

attraction or electromagnetic induction. Regardless of the principle involved, relays are generally

classified according to the function they are called upon to perform in the protection of elelctric

power circuits. For example, a relay which recognises overcurrent in a circuit (i.e. current greater

than that which can be tolerated) and initiates corrective measures would be termed as an overcurrent

relay irrespective of the relay design. Similarly an overvoltage relay is one which recognises overvoltage

in a circuit and initiates the corrective measures. Although there are several types of specialfunction

relays, only the following important types will be discussed in this chapter :

(i) Induction type overcurrent relays

(ii) Induction type reverse power relays

(iii) Distance relays

(iv) Differential relays

(v) Translay scheme

Induction Type Overcurrent Relay (non-directional)

This type of relay works on the induction principle and initiates corrective measures when current in

the circuit exceeds the predetermined value. The actuating source is a current in the circuit supplied

to the relay from a current transformer. These relays are used on a.c. circuits only and can operate for

fault current flow in either direction.

Constructional details. Fig. 21.17 shows the important constructional details of a typical nondirectional

induction type overcurrent relay. It consists of a metallic (aluminium) disc which is free to

rotate inbetween the poles of two electromagnets. The upper electromagnet has a primary and a

secondary winding. The primary is connected to the secondary of a C.T. in the line to be protected

and is tapped at intervals. The tappings are connected to a plug-setting bridge by which the number

of active turns on the relay operating coil can be varied, thereby giving the desired current setting.

The secondary winding is energised by induction from primary and is connected in series with the

winding on the lower magnet. The controlling torque is provided by a spiral spring.

The spindle of the disc carries a moving contact which bridges two fixed contacts (connected to

trip circuit) when the disc rotates through a pre-set angle. This angle can be adjusted to any value

between 0o and 360o. By adjusting this angle, the travel of the moving contact can be adjusted and

hence the relay can be given any desired time setting.

Operation. The driving torque on the aluminium disc is set up due to the induction principle as

discussed in Art. 21.5. This torque is opposed by the restraining torque provided by the spring.

Under normal operating conditions, restraining torque is greater than the driving torque produced by

the relay coil current. Therefore, the aluminium disc remains stationary. However, if the current in

the protected circuit exceeds the pre-set value, the driving torque becomes greater than the restraining

torque. Consequently, the disc rotates and the moving contact bridges the fixed contacts when the

disc has rotated through a pre-set angle. The trip circuit operates the circuit breaker which isolates

the faulty section.

Induction Type Directional Power Relay

This type of relay operates when power in the circuit flows in a specific direction. Unlike a *nondirectional

overcurrent relay, a directional power relay is so designed that it obtains its operating

torque by the interaction of magnetic fields derived from both voltage and current source of the

circuit it protects. Thus this type of relay is essentially a wattmeter and the direction of the torque set

up in the relay depends upon the direction of the current relative to the voltage with which it is

associated.

Constructional details. Fig. 21.18 shows the essential parts of a typical induction type directional

power relay. It consists of an aluminum disc which is free to rotate inbetween the poles of two

electromagnets. The upper electromagnet carries a winding (called potential coil) on the central limb

which is connected through a potential transformer (P.T.) to the circuit voltage source. The lower

electromagnet has a separate winding (called current coil) connected to the secondary of C.T. in the

line to be protected. The current coil is provided with a number of tappings connected to the plugsetting

bridge (not shown for clarity). This permits to have any desired current setting. The restraining

torque is provided by a spiral spring. The spindle of the disc carries a moving contact which bridges two fixed contacts when the disc

has rotated through a pre-set angle. By adjusting this angle, the travel of the moving disc can be

adjusted and hence any desired time-setting can be given to the relay.

Operation. The flux ϕ1 due to current in the potential coil will be nearly 90º lagging behind the

applied voltage V. The flux ϕ2 due to current coil will be nearly in phase with the operating current I

It is clear that the direction of driving torque on the disc depends upon the direction of power

flow in the circuit to which the relay is associated. When the power in the circuit flows in the normal

direction, the driving torque and the restraining torque (due to spring) help each other to turn away

the moving contact from the fixed contacts. Consequently, the relay remains inoperative. However,

the reversal of current in the circuit reverses the direction of driving torque on the disc. When the

reversed driving torque is large enough, the disc rotates in the reverse direction and the moving

contact closes the trip circuit. This causes the operation of the circuit breaker which disconnects the

faulty section.

Induction Type Directional Overcurrent Relay

The directional power relay discussed above is unsuitable for use as a directional protective relay

under short-circuit conditions. When a short-circuit occurs, the system voltage falls to a low value

and there may be *insufficient torque developed in the relay to cause its operation. This difficulty is

overcome in the directional overcurrent relay which is designed to be almost independent of system

voltage and power factor

Constructional details. Fig. 21.19 shows the constructional details of a typical induction type

directional ovecurrent relay. It consists of two relay elements mounted on a common case viz. (i)

directional element and (ii) non-directional element.

(i) Directional element. It is essentially a directional power relay which operates when power

flows in a specific direction. The potential coil of this element is connected through a potential

transformer (P.T.) to the system voltage. The current coil of the element is energised through a C.T.

by the circuit current. This winding is carried over the upper magnet of the non-directional element.

The trip contacts (1 and 2) of the directional element are connected in series with the secondary

circuit of the overcurrent element. Therefore, the latter element cannot start to operate until its

secondary circuit is completed. In other words, the directional element must operate first (i.e. contacts

1 and 2 should close) in order to operate the overcurrent element.

(ii) Non-directional element. It is an overcurrent element similar in all respects to a non-directional

overcurrent relay described in Art. 21.11. The spindle of the disc of this element carries a

moving contact which closes the fixed contacts (trip circuit contacts) after the operation of directional

element.

It may be noted that plug-setting bridge is also provided in the relay for current setting but has

been omitted in the figure for clarity and simplicity. The tappings are provided on the upper magnet

of overcurrent element and are connected to the bridge.

Operation. Under normal operating conditions, power flows in the normal direction in the

circuit protected by the relay. Therefore, directional power relay (upper element) does not operate,

thereby keeping the overcurrent element (lower element) unenergised. However, when a short-circuit

occurs, there is a tendency for the current or power to flow in the reverse direction. Should this

happen, the disc of the *upper element rotates to bridge the fixed contacts 1 and 2. This completes

the circuit for overcurrent element. The disc of this element rotates and the moving contact attached

to it closes the trip circuit. This operates the circuit breaker which isolates the faulty section. The two

relay elements are so arranged that final tripping of the current controlled by them is not made till the

following conditions are satisfied :

(i) current flows in a direction such as to operate the directional element.

(ii) current in the reverse direction exceeds the pre-set value.

(iii) excessive current persists for a period corresponding to the time setting of overcurrent element.

Differential Relays

Most of the relays discussed so far relied on excess of current for their operation. Such relays are less

sensitive because they cannot make correct distinction between heavy load conditions and minor

fault conditions. In order to overcome this difficulty, differential relays are used.

differential relay is one that operates when the phasor difference of two or more similar

electrical quantities exceeds a pre-determined value.

Thus a current differential relay is one that compares the current entering a section of the system

with the current leaving the section. Under normal operating conditions, the two currents are equal

but as soon as a fault occurs, this condition no longer applies. The difference between the incoming

and outgoing currents is arranged to flow through the operating coil of the relay. If this differential

current is equal to or greater than the pickup value, the relay will operate and open the circuit breaker

to isolate the faulty section.

It may be noted that almost any type of relay when connected in a particular way can be made to

operate as a differential relay. In other words, it is not so much the relay construction as the way the

relay is connected in a circuit that makes it a differential relay. There are two fundamental systems of

differential or balanced protection viz.

- Current balance protection (ii) Voltage balance protection

Current Differential Relay

Fig. 21.23 shows an arrangement of an overcurrent relay connected to operate as a differential relay.

A pair of  identical current transformers are fitted on either end of the section to be protected (alternator

winding in this case). The secondaries of CT’s are connected in series in such a way that they

carry the induced currents in the same direction. The operating coil of the overcurrent relay is connected

across the CT secondary circuit. This differential relay compares the current at the two ends of the alternator winding.

Under normal operating conditions, suppose the alternator winding carries a normal current of

1000 A. Then the currents in the two secondaries of CT’s are equal [See Fig. 21.23]. These currents

will merely circulate between the two CT’s and no current will flow through the differential relay.

Therefore, the relay remains inoperative. If a ground fault occurs on the alternator winding as shown

in Fig. 21.24 (i), the two secondary currents will not be equal and the current flows through the

operating coil of the relay, causing the relay to operate. The amount of current flow through the relay

will depend upon the way the fault is being fed.

(i) If some current (500 A in this case) flows out of one side while a larger current (2000 A)

enters the other side as shown in Fig. 21.24 (i), then the difference of the CT secondary

currents i.e. 10 2·5 = 7·5 A will flow through the relay.

(ii) If current flows to the fault from both sides as shown in Fig. 21.24 (ii), then sum of CT

secondary currents i.e. 10 + 5 = 15 A will flow through the relay.

Disadvantages

(i) The impedance of the *pilot cables generally causes a slight difference between the currents

at the two ends of the section to be protected. If the relay is very sensitive, then the small

differential current flowing through the relay may cause it to operate even under no fault

conditions.

(ii) Pilot cable capacitance causes incorrect operation of the relay when a large through-current

flows.

(iii) Accurate matching of current transformers cannot be achieved due to pilot circuit impedance.

The above disadvantages are overcome to a great extent in biased beam relay.

Voltage Balance Differential Relay

Fig. 21.27 shows the arrangement of voltage balance protection. In this scheme of protection, two

similar current transformers are connected at either end of the element to be protected (e.g. an alternator

winding) by means of pilot wires. The secondaries of current transformers are connected in

series with a relay in such a way that under normal conditions, their induced e.m.f.s’ are in opposition.

Under healthy conditions, equal currents (I1 = I2) flow in both primary windings. Therefore, the

secondary voltages of the two transformers are balanced against each other and no current will flow

through the relay operating coil. When a fault occurs in the protected zone, the currents in the two

primaries will differ from one another (i.e. I1 not equals toI2) and their secondary voltages will no longer be in

balance. This voltage †difference will cause a current to flow through the operating coil of the relay

which closes the trip circuit.

Disadvantages

The voltage balance system suffers from the following drawbacks :

(i) A multi-gap transformer construction is required to achieve the accurate balance between

current transformer pairs.

(ii) The system is suitable for protection of cables of relatively short lengths due to the capacitance

of pilot wires. On long cables, the charging current may be sufficient to operate the

relay even if a perfect balance of current transformers is attained.

The above disadvantages have been overcome in Translay (modified) balanced voltage system.

Types of Protection

When a fault occurs on any part of electric power system, it must be cleared quickly in order to avoid

damage and/or interference with the rest of the system. It is a usual practice to divide the protection

scheme into two classes viz. primary protection and back-up protection.

(i) Primary Protection. It is the protection scheme which is designed to protect the component

parts of the power system. Thus referring to Fig. 21.29, each line has an overcurrent

relay that protects the line. If a fault occurs on any line, it will be cleared by its relay and

circuit breaker. This forms the primary or main protection and serves as the first line of

defence. The service record of primary relaying is very high with well over ninety percent

of all operations being correct. However, sometimes faults are not cleared by primary relay

system because of trouble within the relay, wiring system or breaker. Under such conditions,

back-up protection does the required job.

(ii) Back-up protection. It is the second line of defence in case of failure of the primary protection.

It is designed to operate with sufficient time delay so that primary relaying will be

given enough time to function if it is able to. Thus referring to Fig. 21.29, relay A provides

back-up protection for each of the four lines. If a line fault is not cleared by its relay and

breaker, the relay A on the group breaker will operate after a definite time delay and clear the

entire group of lines. It is evident that when back-up relaying functions, a larger part is

disconnected than when primary relaying functions correctly. Therefore, greater emphasis

should be placed on the better maintenance of primary relaying.